## A
Capacitor Bank Design and Protection | [5 empty] | Bruce Mork |  | 2007-04-11
| Externally Fused Configuration Only! |  |  |  |  | Michigan Tech University - Teaching Example
Bank Specification: |  |  |  |  | Can Specs:
[6 empty] | Voltage: |  | 13.28 | kV
Grounded-Wye Bank | [5 empty] | Rating: |  | 200 | kVAR
[6 empty] | Loss: |  | 0.1 | W/kVAR
L-L System Voltage: |  | 138 | kV |  |  | Capacitance: |  | 3.0082 | uFarads
Size of Bank: |  | 80 | MVAR |  |  | Impedance: |  | 881.792 | Ohms
[6 empty] | Current: |  | 15.0602 | Amps
[6 empty] | Diss Ohms: |  | 8.8179 | MOhms
Configuration:
|  |  |  | Calc | Chosen
| Total No. Cans: |  |  | 400 | 414 | Cans
| No. Cans/Phase: |  |  | 133.3333 | 138 | Cans/Ph
| Series Groups/Phase: |  |  | 5.9996 | 6
| Parallel Cans/Group: |  |  | 22.2238 | 23
| Impedance/Group: |  |  |  | 38.3388 | Ohms
| Impedance/Phase: |  |  |  | 230.0327 | Ohms
| Diss Ohms/Phase: |  |  |  | 2.3003 | MOhms
| Discharge RC Time Constant: |  |  |  | 26.5258 | Secs
Performance:
| System Voltage, pu: |  | 0.95 | 1 | 1.05
| Total MVAR |  | 74.7164 | 82.7882 | 91.274
| Line Current, Amps: |  | 329.0429 | 346.3609 | 363.679
| Voltage/Group, kV: |  | 12.6151 | 13.2791 | 13.943
| Voltage/Group, pu: |  | 0.94993 | 0.99993 | 1.0499
| Losses, kW: |  | 7.4716 | 8.2788 | 9.1274 | kW
| Dischg Time to 50V: |  | 203.4255 | 204.7861 | 206.0803 | Seconds
Group Voltages: | [7 empty] | kV | V
[7 empty] | VT Ratio: | 13.2791 | 120
1 | Blown Fuses
| This Group: |  | 13.0894 | 13.7783 | 14.4672 | kV
|  |  | 0.98564 | 1.0375 | 1.0894 | Per Unit
|  |  | 118.2857 | 124.5113 | 130.7368 | VT Sec Volts
| Other Groups: |  | 12.5203 | 13.1792 | 13.8382 | kV
|  |  | 0.94279 | 0.99241 | 1.042 | Per Unit
|  |  | 113.1429 | 119.0977 | 125.0526 | VT Sec Volts
3 | Blown Fuses
| This Group: |  | 14.1535 | 14.8985 | 15.6434 | kV
|  |  | 1.0658 | 1.1219 | 1.178 | Per Unit
|  |  | 127.9024 | 134.6341 | 141.3659 | VT Sec Volts
| Other Groups: |  | 12.3074 | 12.9552 | 13.6029 | kV
|  |  | 0.92676 | 0.97554 | 1.0243 | Per Unit
|  |  | 111.2195 | 117.0732 | 122.9268 | VT Sec Volts
4 | Blown Fuses
| This Group: |  | 14.7533 | 15.5297 | 16.3062 | kV
|  |  | 1.1109 | 1.1694 | 1.2279 | Per Unit
|  |  | 133.322 | 140.339 | 147.3559 | VT Sec Volts
| Other Groups: |  | 12.1875 | 12.8289 | 13.4704 | kV
|  |  | 0.91773 | 0.96603 | 1.0143 | Per Unit
|  |  | 110.1356 | 115.9322 | 121.7288 | VT Sec Volts