## A
Three-Winding Y-Y-D AutoTransformer - Interpretation of Factory Test Data | [7 empty] | Educational Use Only!
Bruce Mork, Jun 25, 2005 |  |  |  | C:\RSCH\XFMR\3WIND.xls |  |  |  | = Input Data
(All other cells are locked)
Winding Ratings, OA | [7 empty] | Freq, Hz | Omega
| kVL-L | MVA | Current | ZBASE, RATED | ZBASE, 100 | ZBASE, TER |  | 60 | 376.9911
H | 345 | 296 | 495.3498 | 402.1115 | 1190.25 | 1545.7792
X | 118 | 296 | 1448.2685 | 47.0405 | 139.24 | 180.8312
Y | 13.8 | 77 | 3221.4472 | 2.4732 | 1.9044 | 2.4732
Binary Short Circuit Tests (Using Base of Source Winding):
Source | Shorted | Test MVA | ISOURCE | ISHORT | PMEAS | R, Ohms | QCALC | %ZMEAS | %RCALC | %XCALC
345 | 118 | 296 | 495.3498 | 1448.2685 | 376940 | 0.51207 | 18377734.7569 | 6.21% | 0.1273% | 6.209% | H-X
345 | 13.8 | 77 | 128.8579 | 3221.4472 | 95448 | 1.9161 | 43042894.1717 | 55.9% | 0.124% | 55.9% | H-Y
118 | 13.8 | 77 | 376.7455 | 3221.4472 | 96588 | 0.22683 | 32416856.1054 | 42.1% | 0.1254% | 42.1% | X-Y
On 100-MVA Base: |  | ZHX = |  |  |  |  | 48.7551 | 2.098% | 0.04302% | 2.098%
|  | ZHY = |  |  |  | X/R = | 450.9565 | 72.6% | 0.161% | 72.6%
|  | ZXY = |  |  |  |  | 335.6199 | 54.68% | 0.1629% | 54.68%
Calculate 3-Winding Star-Equivalent Short-Circuit Impedances:
% on 100-MVA Base
Terminal |  |  | R, Ohms | PAC | P Check |  |  |  | %R | %X
H |  |  | 0.24459 | PHX = | 376940 |  |  | ZH | 0.02055% | 10.01%
X |  |  | 0.03129 | PHY = | 95448 |  |  | ZX | 0.02247% | -7.912%
Y | (Y-Equiv) |  | 0.0026745 | PXY = | 96588 |  |  | ZY | 0.1404% | 62.59%
Ratings of Actual Coils, OA
| kVPH | MVA | Current | ZBASE, RATED | ZBASE, 100 | ZBASE, TER
S | 131.0585 | 64.9198 | 495.3498 | 264.5777 | 515.29 | 669.2078
C | 68.1273 | 64.9198 | 952.9187 | 71.4933 | 139.24 | 180.8312
D | 13.8 | 25.6667 | 1859.9034 | 7.4197 | 5.7132 | 7.4197
Calculate Autotransformer Coil Impedances Based on Conservation of Short-Circuit P & Q:
Coil | IRATED | KVRATED | R, Ohms | X, Ohms | PAC | P Check | QAC | Q Check | VA Chk
Series | 495.3498 | 131.0585 | 0.33608 | 86.9311 | PHX = | 376940 | QHX = | 18377734.7569 | 18381600
Common | 952.9187 | 68.1273 | 0.047556 | -16.744 | PHY = | 95448 | QHY = | 43042894.1717 | 43043000
Delta | 1859.9034 | 13.8 | 0.007356 | 3.8107 | PXY = | 96588 | QXY = | 32416856.1054 | 32417000
Short-Circuit Test Conditions in Each Coil:
Test: |  | H-X |  |  | H-Y |  |  | X-Y
Coil | KVRATED | Isc | MVATEST | PCOIL,KW | Isc | MVATEST | PCOIL,KW | Isc | MVATEST | PCOIL,KW
Series | 131.0585 | 495.3498 | 194.7594 | 247.39 | 128.8579 | 50.6638 | 16.741 | 0.0012396 | 0.00048737 | 1.5492e-09
Common | 68.1273 | 952.9187 | 194.7594 | 129.55 | 128.8579 | 26.3362 | 2.3689 | 376.7455 | 77 | 20.2499
Delta | 13.8 | 0 | 0 | 0 | 1859.9034 | 77 | 76.3381 | 1859.9034 | 77 | 76.3381
|  |  | Total PSC : | 376.94 |  | Total PSC : | 95.448 |  | Total PSC : | 96.588
Synthesized Short-Circuit Tests for S-C-D windings:
Test: |  | S-C |  |  | S-D |  |  | C-D
Coil | KVRATED | Isc | MVATEST | PCOIL,KW | Isc | MVATEST | PCOIL,KW | Isc | MVATEST | PCOIL,KW
Series | 131.0585 | 495.3498 | 194.7594 | 247.39 | 195.8413 | 77 | 38.6693 | 0 | 0 | 0
Common | 68.1273 | 952.9187 | 194.7594 | 129.55 | 0 | 0 | 0 | 376.7455 | 77 | 20.2499
Delta | 13.8 | 0 | 0 | 0 | 1859.9034 | 77 | 76.3381 | 1859.9034 | 77 | 76.3381
|  |  | Total PSC : | 376.94 |  | Total PSC : | 115.0075 |  | Total PSC : | 96.588
S-D
[5 empty] | Isc | MVATEST | PCOIL,KW
[5 empty] | 195.8413 | 77 | 38.6693
[5 empty] | 0 | 0 | 0
[5 empty] | 1859.9034 | 77 | 76.3381
S-C | 1.9237 |  |  |  |  | Total PSC : | 115.0075
S-D | 9.497 |  |  |  |  | ZIN,PU | 1.9305
[6 empty] | ZBASE,S | 223.0693
Details of Synthesized Binary Short Circuit Tests for S-C-D windings (Using Base of Source Winding):
Source | Shorted | Test MVA | ISOURCE | ISHORT | PCALC | QCALC | R, Ohms | X, Ohms | %ZCALC | %RCALC | %XCALC
131.0585 | 68.1273 | 194.7594 | 495.3498 | 952.9187 | 376940 | 18377734.7569 | 0.51207 | 24.9659 | 9.438% | 0.1935% | 9.436% | S-C
131.0585 | 13.8 | 77 | 195.8413 | 1859.9034 | 115007.4699 | 49549077.0024 | 0.99953 | 430.6315 | 64.35% | 0.1494% | 64.35% | S-D
68.1273 | 13.8 | 77 | 376.7455 | 1859.9034 | 96588 | 32416856.1054 | 0.22683 | 76.1296 | 42.1% | 0.1254% | 42.1% | C-D
On 100-MVA Base: |  | ZSC = | [5 empty] | 48.7551 | 4.846% | 0.09937% | 4.845%
|  | ZSD = |  |  |  |  | X/R = | 430.8336 | 83.57% | 0.194% | 83.57%
|  | ZCD = | [5 empty] | 335.6199 | 54.68% | 0.1629% | 54.68%
Calculate 3-Winding Star- and Delta-Equivalent Short-Circuit Impedances: | [7 empty] | % on 100-MVA Base
[8 empty] | %R | %X
[7 empty] | ZS | 0.06522% | 16.87%
Coil Resitances: |  |  | Calculate [A] matrix: |  |  |  | ZC | 0.03415% | -12.03%
|  |  | S | C | D |  | ZD | 0.1288% | 66.7% | L-1 | Referred
RS, OHMS | 0.33608 | S | 33.2527 | -78.0386 | 69.4576 |  | ZS-C | 0.1167% | 1.803% | 150.1252 | C
RC, OHMS | 0.047556 | C | -78.0386 | 188.0958 | -187.4523 |  | ZS-D | 0.4398% | -10% | -659.6384 | D
RD, OHMS | 0.007356 | D | 69.4576 | -187.4523 | 265.7692 |  | ZC-D | 0.2303% | 7.13% | 925.4076 | D
|  |  | VD : VC | 0.20256 |  |  | XS-C // (XS-D + XC-D) |  | 4.845% | \
|  |  | VD : VS | 0.1053 |  |  | XS-D // (XS-C + XC-D) |  | 83.57% | ¦ == Check
|  |  | VC : VS | 0.51982 |  |  | XC-D // (XS-C + XS-D) |  | 54.68% | /
DC Resistance Measurements:
(From factory Report) |  |  | Calculated Values: |  |  |  |  | % Extra
Winding | 3 x RMEAS |  | Coil | R, Ohms |  | PDC | P Check | 60 Hz
"H" | 0.6356 |  | Series | 0.21187 |  | PHX = | 317410.0766 | 18.75%
"X" | 0.1778 |  | Common | 0.059267 |  | PHY = | 85804.1105 | 11.24%
"Y" | 0.0209 |  | Delta | 0.0069667 |  | PXY = | 97534.5594 | -0.9705%
10553.7279
2952.2543
72298.1283